## Calculator
SLOPE METHOD: Calculation of S electrode placement
H (ft) | 90
R1 20% (ft) | 18 | 58.15 | Ω
R2 40% (ft) | 36 | 60.2 | Ω
R3 60% (ft) | 54 | 61.1 | Ω
Slope (µ) = | 0.43902 | µ = (R3-R2)/(R2-R1)
PT/C | 0.6376
S = | 57.384 | ft S = H*X
1. Enter the distance for the H electrode placement in yellow cell B9
2. Enter the 20, 40 and 60% resistance measurements in yellow cells C10, C11, and C12
(Red cells B10, B11, B12, and B14 are protected. You cannot enter data in them.)
3. Take note of the calculated slope-variation coefficient µ in cell C14
4. On the Table tab look for the value PT/C correspondoing to the "µ" coefficient
Orange cell B16 is the calculated result which indicates the location for the S electrode
placement to obtain the ground resistance reading.

## Table
Values of PT/C for various values of µ
µ | 0.XX0 | 0.XX1 | 0.XX2 | 0.XX3 | 0.XX4 | 0.XX5 | 0.XX6 | 0.XX7 | 0.XX8 | 0.XX9
0.4 | 0.6432 | 0.6431 | 0.6429 | 0.6428 | 0.6426 | 0.6425 | 0.6423 | 0.6422 | 0.642 | 0.6419
0.41 | 0.6418 | 0.6416 | 0.6415 | 0.6413 | 0.6412 | 0.641 | 0.6409 | 0.6408 | 0.6406 | 0.6405
0.42 | 0.6403 | 0.6402 | 0.64 | 0.6399 | 0.6397 | 0.6396 | 0.6395 | 0.6393 | 0.6392 | 0.639 | For example, this value
0.43 | 0.6389 | 0.6387 | 0.6386 | 0.6384 | 0.6383 | 0.6381 | 0.638 | 0.6378 | 0.6377 | 0.6376 | belongs to µ=0.439
0.44 | 0.6374 | 0.6373 | 0.6372 | 0.637 | 0.6369 | 0.6367 | 0.6366 | 0.6364 | 0.6363 | 0.6361
0.45 | 0.636 | 0.6359 | 0.6357 | 0.6356 | 0.6354 | 0.6353 | 0.6351 | 0.635 | 0.6348 | 0.6347
0.46 | 0.6346 | 0.6344 | 0.6343 | 0.6341 | 0.634 | 0.6338 | 0.6337 | 0.6336 | 0.6334 | 0.6333
0.47 | 0.6331 | 0.633 | 0.6328 | 0.6327 | 0.6325 | 0.6324 | 0.6323 | 0.6321 | 0.632 | 0.6318
0.48 | 0.6317 | 0.6315 | 0.6314 | 0.6312 | 0.6311 | 0.631 | 0.6308 | 0.6307 | 0.6305 | 0.6304
0.49 | 0.6302 | 0.6301 | 0.63 | 0.6298 | 0.6297 | 0.6295 | 0.6294 | 0.6292 | 0.6291 | 0.6289
0.5 | 0.6288 | 0.6286 | 0.6285 | 0.6283 | 0.6282 | 0.628 | 0.6279 | 0.6277 | 0.6276 | 0.6274
0.51 | 0.6273 | 0.6271 | 0.6269 | 0.6268 | 0.6266 | 0.6265 | 0.6263 | 0.6262 | 0.626 | 0.6259
0.52 | 0.6258 | 0.6257 | 0.6255 | 0.6254 | 0.6252 | 0.6251 | 0.6249 | 0.6248 | 0.6246 | 0.6245
0.53 | 0.6244 | 0.6243 | 0.6241 | 0.624 | 0.6238 | 0.6237 | 0.6235 | 0.6234 | 0.6232 | 0.6231
0.54 | 0.623 | 0.6229 | 0.6227 | 0.6226 | 0.6224 | 0.6223 | 0.6221 | 0.622 | 0.6218 | 0.6217
0.55 | 0.6216 | 0.6215 | 0.6213 | 0.6212 | 0.621 | 0.6209 | 0.6207 | 0.6206 | 0.6204 | 0.6203
0.56 | 0.6202 | 0.6201 | 0.6199 | 0.6198 | 0.6196 | 0.6195 | 0.6193 | 0.6192 | 0.619 | 0.6189
0.57 | 0.6188 | 0.6187 | 0.6185 | 0.6184 | 0.6182 | 0.6181 | 0.6179 | 0.6178 | 0.6176 | 0.6175
0.58 | 0.6174 | 0.6173 | 0.6171 | 0.617 | 0.6168 | 0.6167 | 0.6165 | 0.6164 | 0.6162 | 0.6161
0.59 | 0.616 | 0.6159 | 0.6157 | 0.6156 | 0.6154 | 0.6153 | 0.6151 | 0.615 | 0.6148 | 0.6147
0.6 | 0.6146 | 0.6145 | 0.6143 | 0.6142 | 0.614 | 0.6139 | 0.6137 | 0.6136 | 0.6134 | 0.6133
0.61 | 0.6132 | 0.6131 | 0.6129 | 0.6128 | 0.6126 | 0.6125 | 0.6123 | 0.6122 | 0.612 | 0.6119
0.62 | 0.6118 | 0.6117 | 0.6115 | 0.6114 | 0.6112 | 0.6111 | 0.6109 | 0.6108 | 0.6106 | 0.6105
0.63 | 0.6104 | 0.6103 | 0.6101 | 0.61 | 0.6098 | 0.6097 | 0.6095 | 0.6094 | 0.6092 | 0.6091
0.64 | 0.6071 | 0.607 | 0.6068 | 0.6066 | 0.6065 | 0.6063 | 0.6061 | 0.606 | 0.6058 | 0.6057
0.65 | 0.6055 | 0.6053 | 0.6052 | 0.605 | 0.6049 | 0.6047 | 0.6045 | 0.6044 | 0.6042 | 0.604
0.66 | 0.6039 | 0.6037 | 0.6036 | 0.6034 | 0.6032 | 0.6031 | 0.6029 | 0.6027 | 0.6026 | 0.6024
0.67 | 0.6023 | 0.6021 | 0.6019 | 0.6018 | 0.6016 | 0.6015 | 0.6013 | 0.6011 | 0.601 | 0.6008
0.68 | 0.6006 | 0.6005 | 0.6003 | 0.6002 | 0.6 | 0.5098 | 0.5997 | 0.5995 | 0.5993 | 0.5992
0.69 | 0.599 | 0.5989 | 0.5987 | 0.5985 | 0.5984 | 0.5982 | 0.598 | 0.5979 | 0.5977 | 0.5976
0.7 | 0.5974 | 0.5973 | 0.5971 | 0.5969 | 0.5967 | 0.5965 | 0.5964 | 0.5962 | 0.596 | 0.5959
0.71 | 0.5957 | 0.5955 | 0.5953 | 0.5952 | 0.595 | 0.5948 | 0.5947 | 0.5945 | 0.5943 | 0.5942
0.72 | 0.594 | 0.5938 | 0.5936 | 0.5935 | 0.5933 | 0.5931 | 0.593 | 0.5928 | 0.5926 | 0.5924
0.73 | 0.5923 | 0.5921 | 0.592 | 0.5918 | 0.5916 | 0.5914 | 0.5912 | 0.5911 | 0.5909 | 0.5907
0.74 | 0.5906 | 0.5904 | 0.5902 | 0.59 | 0.5899 | 0.5897 | 0.5895 | 0.5894 | 0.5892 | 0.589
0.75 | 0.5889 | 0.5887 | 0.5885 | 0.5883 | 0.5882 | 0.588 | 0.5878 | 0.5877 | 0.5875 | 0.5873
0.76 | 0.5871 | 0.587 | 0.5868 | 0.5866 | 0.5865 | 0.5863 | 0.5861 | 0.5859 | 0.5858 | 0.5856
0.77 | 0.5854 | 0.5853 | 0.5851 | 0.5849 | 0.5847 | 0.5846 | 0.5844 | 0.5842 | 0.5841 | 0.5839
0.78 | 0.5837 | 0.5835 | 0.5834 | 0.5832 | 0.583 | 0.5829 | 0.5827 | 0.5825 | 0.5824 | 0.5822
0.79 | 0.582 | 0.5818 | 0.5817 | 0.5815 | 0.5813 | 0.5812 | 0.581 | 0.5808 | 0.5806 | 0.5805
0.8 | 0.5803 | 0.5801 | 0.5799 | 0.5797 | 0.5796 | 0.5794 | 0.5792 | 0.579 | 0.5788 | 0.5786
0.81 | 0.5785 | 0.5783 | 0.5781 | 0.5779 | 0.5777 | 0.5775 | 0.5773 | 0.5772 | 0.577 | 0.5768
0.82 | 0.5766 | 0.5764 | 0.5762 | 0.576 | 0.5759 | 0.5757 | 0.5755 | 0.5753 | 0.5751 | 0.5749
0.83 | 0.5748 | 0.5746 | 0.5744 | 0.5742 | 0.574 | 0.5738 | 0.5736 | 0.5735 | 0.5733 | 0.5731
0.84 | 0.5729 | 0.5727 | 0.5725 | 0.5723 | 0.5722 | 0.572 | 0.5718 | 0.5716 | 0.5714 | 0.5712
0.85 | 0.5711 | 0.5709 | 0.5707 | 0.5705 | 0.5703 | 0.5701 | 0.5699 | 0.5698 | 0.5696 | 0.5694
0.86 | 0.5692 | 0.569 | 0.5688 | 0.5686 | 0.5685 | 0.5683 | 0.5681 | 0.5679 | 0.5677 | 0.5675
0.87 | 0.5674 | 0.5672 | 0.567 | 0.5668 | 0.5666 | 0.5664 | 0.5662 | 0.5661 | 0.5659 | 0.5657
0.88 | 0.5655 | 0.5653 | 0.5651 | 0.565 | 0.5648 | 0.5646 | 0.5644 | 0.5642 | 0.564 | 0.5638
0.89 | 0.5637 | 0.5635 | 0.5633 | 0.5631 | 0.5629 | 0.5627 | 0.5625 | 0.5624 | 0.5622 | 0.562
0.9 | 0.5618 | 0.5616 | 0.5614 | 0.5612 | 0.561 | 0.5608 | 0.5606 | 0.5604 | 0.5602 | 0.56
0.91 | 0.5598 | 0.5596 | 0.5594 | 0.5592 | 0.559 | 0.5588 | 0.5586 | 0.5584 | 0.5582 | 0.558
0.92 | 0.5578 | 0.5576 | 0.5574 | 0.5572 | 0.557 | 0.5568 | 0.5565 | 0.5563 | 0.5561 | 0.5559
0.93 | 0.5557 | 0.5555 | 0.5553 | 0.5551 | 0.5549 | 0.5547 | 0.5545 | 0.5543 | 0.5541 | 0.5539
0.94 | 0.5537 | 0.5535 | 0.5533 | 0.5531 | 0.5529 | 0.5527 | 0.5525 | 0.5523 | 0.5521 | 0.5519
0.95 | 0.5517 | 0.5515 | 0.5513 | 0.5511 | 0.5509 | 0.55 | 0.5505 | 0.5503 | 0.5501 | 0.5499
0.96 | 0.5497 | 0.5495 | 0.5493 | 0.5491 | 0.5489 | 0.5487 | 0.5485 | 0.5483 | 0.5481 | 0.5479
0.97 | 0.5477 | 0.5475 | 0.5473 | 0.5471 | 0.5469 | 0.5467 | 0.5464 | 0.5462 | 0.546 | 0.5458
0.98 | 0.5456 | 0.5454 | 0.5452 | 0.545 | 0.5448 | 0.5446 | 0.5444 | 0.5442 | 0.544 | 0.5438
0.99 | 0.5436 | 0.5434 | 0.5432 | 0.543 | 0.5428 | 0.5426 | 0.5424 | 0.5422 | 0.542 | 0.5418
1 | 0.5416 | 0.5414 | 0.5412 | 0.5409 | 0.5407 | 0.5405 | 0.5403 | 0.54 | 0.5398 | 0.5396
1.01 | 0.5394 | 0.5391 | 0.5389 | 0.5387 | 0.5385 | 0.5383 | 0.538 | 0.5378 | 0.5376 | 0.5374
1.02 | 0.5371 | 0.5369 | 0.5367 | 0.5365 | 0.5362 | 0.536 | 0.5358 | 0.5356 | 0.5354 | 0.5351
1.03 | 0.5349 | 0.5347 | 0.5345 | 0.5344 | 0.534 | 0.5338 | 0.5336 | 0.5333 | 0.5331 | 0.5329
1.04 | 0.5327 | 0.5325 | 0.5322 | 0.532 | 0.5318 | 0.5316 | 0.5313 | 0.5311 | 0.5309 | 0.5307
1.05 | 0.5305 | 0.5302 | 0.53 | 0.5298 | 0.5296 | 0.5293 | 0.5291 | 0.5289 | 0.5287 | 0.5284
1.06 | 0.5282 | 0.528 | 0.5278 | 0.5276 | 0.5273 | 0.5271 | 0.5269 | 0.5267 | 0.5264 | 0.5262
1.07 | 0.526 | 0.5258 | 0.5255 | 0.5253 | 0.5251 | 0.5249 | 0.5247 | 0.5244 | 0.5242 | 0.524
1.08 | 0.5238 | 0.5235 | 0.5233 | 0.5231 | 0.5229 | 0.5229 | 0.5224 | 0.5222 | 0.5219 | 0.5217
1.09 | 0.5215 | 0.5213 | 0.5211 | 0.5209 | 0.5206 | 0.5204 | 0.5202 | 0.52 | 0.5197 | 0.5195
1.1 | 0.5193 | 0.519 | 0.5188 | 0.5185 | 0.5183 | 0.518 | 0.5178 | 0.5175 | 0.5173 | 0.517
1.11 | 0.5168 | 0.5165 | 0.5163 | 0.516 | 0.5158 | 0.5155 | 0.5153 | 0.515 | 0.5148 | 0.5145
1.12 | 0.5143 | 0.514 | 0.5137 | 0.5135 | 0.5132 | 0.513 | 0.5127 | 0.5125 | 0.5122 | 0.512
1.13 | 0.5118 | 0.5115 | 0.5113 | 0.511 | 0.5108 | 0.5105 | 0.5103 | 0.51 | 0.5098 | 0.5095
1.14 | 0.5093 | 0.509 | 0.5088 | 0.5085 | 0.5083 | 0.508 | 0.5078 | 0.5075 | 0.5073 | 0.507
1.15 | 0.5068 | 0.5065 | 0.5062 | 0.506 | 0.5057 | 0.5055 | 0.5052 | 0.505 | 0.5047 | 0.5045
1.16 | 0.5042 | 0.504 | 0.5037 | 0.5035 | 0.5032 | 0.503 | 0.5027 | 0.5025 | 0.5022 | 0.502
1.17 | 0.5017 | 0.5015 | 0.5012 | 0.501 | 0.5007 | 0.5005 | 0.5002 | 0.5 | 0.5997 | 0.4995
1.18 | 0.4992 | 0.499 | 0.4987 | 0.4985 | 0.4982 | 0.498 | 0.4977 | 0.4975 | 0.4972 | 0.497
1.19 | 0.4967 | 0.4965 | 0.4962 | 0.496 | 0.4957 | 0.4955 | 0.4952 | 0.495 | 0.4947 | 0.4945
1.2 | 0.4942 | 0.4939 | 0.4936 | 0.4933 | 0.493 | 0.4928 | 0.4925 | 0.4922 | 0.4919 | 0.4916
1.21 | 0.4913 | 0.491 | 0.4907 | 0.4904 | 0.4901 | 0.4899 | 0.4896 | 0.4893 | 0.489 | 0.4887
1.22 | 0.4884 | 0.4881 | 0.4878 | 0.4875 | 0.4872 | 0.487 | 0.4867 | 0.4864 | 0.4861 | 0.4858
1.23 | 0.4855 | 0.4852 | 0.4849 | 0.4846 | 0.4843 | 0.4841 | 0.4838 | 0.4835 | 0.4832 | 0.4829
1.24 | 0.4826 | 0.4823 | 0.482 | 0.4817 | 0.4814 | 0.4812 | 0.4809 | 0.4806 | 0.4803 | 0.48
1.25 | 0.4797 | 0.4794 | 0.4791 | 0.4788 | 0.4785 | 0.4783 | 0.478 | 0.4777 | 0.4774 | 0.4771
1.26 | 0.4768 | 0.4765 | 0.4762 | 0.4759 | 0.4756 | 0.4754 | 0.4751 | 0.4748 | 0.4745 | 0.4742
1.27 | 0.4739 | 0.4736 | 0.4733 | 0.473 | 0.4727 | 0.4725 | 0.4722 | 0.4719 | 0.4716 | 0.4713
1.28 | 0.471 | 0.4707 | 0.4704 | 0.4701 | 0.4698 | 0.4696 | 0.4693 | 0.469 | 0.4687 | 0.4684
1.29 | 0.4681 | 0.4678 | 0.4675 | 0.4672 | 0.4669 | 0.4667 | 0.4664 | 0.4661 | 0.4658 | 0.4655
1.3 | 0.4652 | 0.4649 | 0.4645 | 0.4642 | 0.4638 | 0.4635 | 0.4631 | 0.4628 | 0.4625 | 0.4621
1.31 | 0.4618 | 0.4614 | 0.4611 | 0.4607 | 0.4604 | 0.4601 | 0.4597 | 0.4594 | 0.459 | 0.4586
1.32 | 0.4583 | 0.458 | 0.4577 | 0.4573 | 0.457 | 0.4566 | 0.4563 | 0.4559 | 0.4556 | 0.4553
1.33 | 0.4549 | 0.4546 | 0.4542 | 0.4539 | 0.4535 | 0.4532 | 0.4529 | 0.4525 | 0.4522 | 0.4518
1.34 | 0.4515 | 0.4511 | 0.4508 | 0.4505 | 0.4501 | 0.4498 | 0.4494 | 0.4491 | 0.4487 | 0.4484
1.35 | 0.4481 | 0.4477 | 0.4474 | 0.447 | 0.4467 | 0.4463 | 0.446 | 0.4457 | 0.4453 | 0.445
1.36 | 0.4446 | 0.4443 | 0.4439 | 0.4436 | 0.4432 | 0.4429 | 0.4426 | 0.4422 | 0.4419 | 0.4415
1.37 | 0.4412 | 0.4408 | 0.4405 | 0.4402 | 0.4398 | 0.4395 | 0.5391 | 0.4388 | 0.4384 | 0.4381
1.38 | 0.4378 | 0.4374 | 0.4371 | 0.4367 | 0.4364 | 0.436 | 0.4357 | 0.4354 | 0.435 | 0.4347
1.39 | 0.4343 | 0.434 | 0.4336 | 0.4333 | 0.433 | 0.4326 | 0.4323 | 0.4319 | 0.4316 | 0.4312
1.4 | 0.4309 | 0.4305 | 0.4301 | 0.4296 | 0.4292 | 0.4288 | 0.4284 | 0.428 | 0.4275 | 0.4271
1.41 | 0.4267 | 0.4263 | 0.4258 | 0.4254 | 0.425 | 0.4246 | 0.4242 | 0.4237 | 0.4233 | 0.4229
1.42 | 0.4225 | 0.4221 | 0.4216 | 0.4212 | 0.4208 | 0.4204 | 0.42 | 0.4195 | 0.4191 | 0.4187
1.43 | 0.4183 | 0.4178 | 0.4174 | 0.417 | 0.4166 | 0.4162 | 0.4157 | 0.4153 | 0.4149 | 0.4145
1.44 | 0.4141 | 0.4136 | 0.4132 | 0.4128 | 0.4124 | 0.412 | 0.4115 | 0.4111 | 0.4107 | 0.4103
1.45 | 0.4099 | 0.4094 | 0.409 | 0.4086 | 0.4082 | 0.4077 | 0.4073 | 0.4069 | 0.4065 | 0.4061
1.46 | 0.4056 | 0.4052 | 0.4048 | 0.4044 | 0.404 | 0.4035 | 0.4031 | 0.4027 | 0.4023 | 0.4018
1.47 | 0.4014 | 0.401 | 0.4006 | 0.4001 | 0.3997 | 0.3993 | 0.3989 | 0.3985 | 0.398 | 0.3976
1.48 | 0.3972 | 0.3968 | 0.3964 | 0.3959 | 0.3955 | 0.3951 | 0.3947 | 0.3943 | 0.3938 | 0.3934
1.49 | 0.393 | 0.3926 | 0.3921 | 0.3917 | 0.3913 | 0.3909 | 0.3905 | 0.39 | 0.3896 | 0.3892
1.5 | 0.3888 | 0.3883 | 0.3878 | 0.3874 | 0.3869 | 0.3864 | 0.3859 | 0.3854 | 0.385 | 0.3845
1.51 | 0.384 | 0.3835 | 0.383 | 0.3825 | 0.382 | 0.3816 | 0.3811 | 0.3806 | 0.3801 | 0.3796
1.52 | 0.3791 | 0.3786 | 0.3781 | 0.3776 | 0.3771 | 0.3766 | 0.376 | 0.3755 | 0.375 | 0.3745
1.53 | 0.374 | 0.3735 | 0.373 | 0.3724 | 0.3719 | 0.3714 | 0.3709 | 0.3704 | 0.3698 | 0.3693
1.54 | 0.3688 | 0.3683 | 0.3677 | 0.3672 | 0.3667 | 0.3662 | 0.3656 | 0.3651 | 0.3646 | 0.364
1.55 | 0.3635 | 0.363 | 0.3624 | 0.3619 | 0.3613 | 0.3608 | 0.3602 | 0.3597 | 0.3591 | 0.3586
1.56 | 0.358 | 0.3574 | 0.3569 | 0.3563 | 0.3557 | 0.3552 | 0.3546 | 0.354 | 0.3534 | 0.3528
1.57 | 0.3523 | 0.3517 | 0.4511 | 0.3506 | 0.35 | 0.3494 | 0.3488 | 0.3482 | 0.3477 | 0.3471
1.58 | 0.3465 | 0.3459 | 0.3453 | 0.3447 | 0.3441 | 0.3435 | 0.3429 | 0.3423 | 0.3417 | 0.3411
1.59 | 0.3405 | 0.3399 | 0.3393 | 0.3386 | 0.338 | 0.3374 | 0.3368 | 0.3362 | 0.3355 | 0.3349