## FOP Plot
Test Date
| Instrument Mfg. |  |  |  | Operator Name
| Model |  |  |  |  | Test Location
| Serial # |  |  |  |  | Address
Test Conditions
|  | Soil Condition: |  |  | Moist |  | Dry |  | Temperature |  | °F | °C
[5 empty] | Clay |  | Limestone |  | Sand & Gravel
|  | Soil Type: |  |  | Granite |  | Shale |  | Sandstone
|  | (choose one) |  |  | Loam |  | Slate |  | Other
[5 empty] | Single Rod |  | Rod Depth |  |  | ft
|  | Grounding System: |  |  | Multiple Rod (Grid)
[5 empty] | Longest Diagonal Distance |  |  |  |  | ft
| H Electrode Distance: |  |  | ft
| S Electrode Distance |  | Measured Resistance
| % | Feet | Ohms
| 10 | 0
| 20 | 0
| 30 | 0
| 40 | 0
| 50 | 0
| 60 | 0
| 70 | 0
| 80 | 0
| 90 | 0
[5 empty] | Effective Grounding Electrode Resistance: |  | 0 | Ohms
[5 empty] | Standard Deviation Percent: |  | #DIV/0! | %
Chauvin Arnoux®, Inc. d.b.a. AEMC® Instruments
www.aemc.com ¦ (800) 343-1391 ¦ techsupport@aemc.com
15 Faraday Drive ¦ Dover, NH 03820

## Instructions
Instructions for Fall of Potential Plot Tab
1. Fill in operator and instrument information.
2. Determine and check off test conditions and soil type.
3. Determine grounding system and fill in rod depth or grid diagonal length
4. Determine the distance for the H electrode from the tables below and enter it
into cell D27 (light green box) the S electrode distances will fill in automatically.
5. Enter the test resistance for each S electrode point in cell D31 through cell D39 (light green boxes)
in proper sequence.
The plot will fill in automatically and the average grounding electrode resistance
for the plateau area will fill-in in cell H63 (red cell).
6. Print report and save file using a different name
Approximate distance to
H for single electrode systems
| Depth Driven | Distance to H
| 6 ft | 72 ft
| 8 ft | 80 ft
| 10 ft | 88 ft
| 12 ft | 96 ft
| 18 ft | 115 ft
| 20 ft | 120 ft
| 30 ft | 140 ft
Multiple Electrode System
| Max Grid Distance | Distance to H
| 6 ft | 125 ft
| 8 ft | 140 ft
| 10 ft | 160 ft
| 12 ft | 170 ft
| 14 ft | 190 ft
| 16 ft | 200 ft
| 18 ft | 210 ft
| 20 ft | 220 ft
| 30 ft | 260 ft
| 40 ft | 300 ft
| 50 ft | 340 ft
| 60 ft | 370 ft
| 80 ft | 440 ft
| 100 ft | 500 ft
| 120 ft | 550 ft
| 140 ft | 600 ft
| 160 ft | 630 ft
| 180 ft | 700 ft
| 200 ft | 730 ft
Chauvin Arnoux®, Inc. d.b.a. AEMC® Instruments
www.aemc.com ¦ (800) 343-1391 ¦ techsupport@aemc.com
15 Faraday Drive ¦ Dover, NH 03820

## Example
[12 empty] | Test Date | 2023-08-14
| Instrument Mfg. | AEMC |  |  | Operator Name |  | Joe Ground Tester
| Model | 4630 |  |  |  | Test Location | Building 3C
| Serial # | 124-82 |  |  |  | Address | 15 Faraday Dr. Dover NH 03820
Test Conditions
|  | Soil Condition: |  | X | Moist |  | Dry |  | Temperature | 52 | °F
[5 empty] | Clay |  | Limestone |  | Sand & Gravel
|  | Soil Type: |  |  | Granite |  | Shale |  | Sandstone
|  | (choose one) |  | X | Loam |  | Slate |  | Other
|  |  |  | X | Single Rod |  | Rod Depth |  | 15 | ft
|  | Grounding System: |  |  | Multiple Rod (Grid)
[5 empty] | Longest Diagonal Distance |  |  |  |  | ft
| H Electrode Distance: |  | 100 | ft
| S Electrode Distance |  | Measured Resistance
| % | Feet | Ohms
| 10 | 10 | 6.2
| 20 | 20 | 8.2
| 30 | 30 | 9.5
| 40 | 40 | 10.9
| 50 | 50 | 14.5
| 60 | 60 | 15.1
| 70 | 70 | 16
| 80 | 80 | 28.4
| 90 | 90 | 39
[5 empty] | Effective Grounding Electrode Resistance: |  | 15.2 | Ohms
[5 empty] | % Deviation: |  | 4.967 | %
Chauvin Arnoux®, Inc. d.b.a. AEMC® Instruments
www.aemc.com ¦ (800) 343-1391 ¦ techsupport@aemc.com
15 Faraday Drive ¦ Dover, NH 03820